## Slide 1
M.Tech/MCA Program
Advanced Industry Integrated Programs
Jointly offered by University and LTIMindTree
Review II
GridRecoveryIQ
Agentic Outage Risk Prediction & Restoration Optimisation
Rushikesh Rahul Nirmal
25MML0016 · M.Tech Artificial Intelligence & Machine Learning
VIT Vellore · Jointly offered with LTIMindtree
Knowledge partner | Implementation partner

## Slide 2
An 11 kV distribution feeder is radial — power flows one way, from the substation outward to the ends.
When a fault occurs, protection drops the entire feeder. Thousands of customers lose supply although only one section is physically damaged.
Most of the resulting outage is therefore topological, not physical: healthy load sitting dark purely because of how the network is switched.
Distribution utilities are measured on customer-minutes interrupted, so that avoidable share is the dominant cost of every fault.
Existing outage-management tools report risk on one screen and track crews on another, but take no action in between — which is where the recoverable minutes are.
The gap this project addresses: deciding, automatically and within seconds, which switches to operate so that customers who need no repair are not made to wait for one.
Introduction
GridRecoveryIQ

## Slide 3
Predict section-level outage risk from weather, asset condition and load, calibrated so the probabilities are usable for ranking.
On a fault, isolate the smallest faulted zone and restore stranded healthy load by remote switching, subject to neighbouring-feeder capacity.
Optimise crew dispatch for the residual physical repair against customer-minutes interrupted rather than travel distance.
Expose every decision with an auditable rationale on a live operations dashboard an operator could actually work from.
Quantify the benefit against an explicit no-automation counterfactual run in parallel — a measurement, not a claim.
Scope: a complete working platform on a synthetic but physically reasoned testbed, not a component study.
Objective
GridRecoveryIQ

## Slide 4
RiskSentinel · ranked exposure before anything fails
LightGBM binary classifier over 187 sections × 3-hourly blocks — 1.64 M rows at a 0.216% base rate.
Features: weather exposure, conductor type and age, vegetation index, insulation condition, terrain, load and maintenance history.
Time-ordered train/validation/test split — no shuffling, no leakage across storm events. Isotonic calibration fitted on validation only.
Held-out test ROC-AUC 0.804 against an oracle ceiling of 0.841 — 89% of achievable skill; 10.6× lift in the top 1% of sections.
Per-section drivers from exact TreeSHAP contributions, so every risk number on the dashboard can state what is behind it.
Module 1 — Outage Risk Prediction
GridRecoveryIQ

## Slide 5
SelfHealAgent · the core contribution of this project
Locate the fault, walk the feeder tree to the nearest sectionalising switch, and isolate the smallest zone that contains it.
Reclose the breaker so all load upstream of the fault is restored from its own source.
For each healthy island stranded downstream, enumerate every (tie switch, pickup set) pair that could energise it from a neighbouring feeder.
CP-SAT maximises criticality-weighted customers restored — one tie per island, each tie used once, every donor feeder held under a 92% loading margin.
Partial pickup: where an island exceeds donor headroom, open one of its internal switches and shed its lowest value-per-kVA branch. 9 of 187 fault locations require exactly this.
Across all 187 sections: 66% of affected customers restored on average (median 77%) in a median of 75 seconds — with no crew involved.
Module 2 — Self-Healing Restoration (FLISR)
GridRecoveryIQ

## Slide 6
DispatchAgent · optimising the right objective
The question is not the shortest tour. A utility is judged on customer-minutes, so the model minimises Σ (customers × criticality × completion time).
Weighted-completion-time VRP solved with CP-SAT: per-crew AddCircuit routing, skill matching, travel-time precedence and a greedy warm start.
16 jobs / 5 crews — 48.7% better than nearest-qualified-first, proved optimal in 4.9 s.
30 jobs / 6 crews — 65.2% better, feasible within a 30 s interactive budget.
Live 4-crew cyclone scenario runs 42–50% better than the dispatcher's rule of thumb. A test asserts the optimiser is never worse than the heuristic it replaces.
Module 3 — Crew Dispatch Optimisation
GridRecoveryIQ

## Slide 7
Testbed
Radial 11 kV system over the Vellore region: 4 substations, 11 feeders, 187 switchable sections, 25 tie switches, 64,309 customers, 10 critical sites on real feeder laterals.
Hidden hazard design
Three years of 3-hourly history generated from a physical hazard function — squared wind response gated by vegetation encroachment, lightning gated by insulation condition, soil saturation acting only on underground cable, exponential ageing.
Storms sampled seasonally and swept across the territory, so faults cluster in space and time the way real outage data does.
The model observes only measurable features. It never sees the hazard function.
Agent contract
Deterministic engine computes → agent frames the result → LLM narrates. No figure anywhere in the system originates from the language model.
Methodology / Modelling Plan
GridRecoveryIQ

## Slide 8
Panel of 1.64 M section × time rows carrying 2,550 outage events (~850/yr) at a 0.216% base rate — severe class imbalance, handled by ranking metrics rather than accuracy.
Chronological split by time with no shuffling, so no storm event spans train and test.
Isotonic calibration fitted on validation only; held-out Brier score 0.002141 against an oracle 0.002134 — within 0.3% of optimal calibration.
Parquet columnar storage for the panel; generation is fully seeded, so any rebuild reproduces the same network, the same history and the same model scores.
Data provenance — stated explicitly
The network and outage history are synthetic. Only the geographic centre and the monthly climatology of the Vellore region are drawn from reality. No real utility data is used, and no claim is made about any operating network. The synthetic design is deliberate: because the true hazard is known, the model can be scored against an oracle ceiling — a benchmark that cannot exist on real data.
Data Preprocessing & EDA
GridRecoveryIQ

## Slide 9
Prediction
LightGBM gradient-boosted trees · scikit-learn isotonic calibration and metrics · exact TreeSHAP attribution
Optimisation
Google OR-Tools CP-SAT, used for both problems — tie-switch selection under capacity, and weighted-completion-time crew routing
Grid model
NetworkX — radial feeder trees, upstream/downstream traversal, island detection after switching
Data & service
NumPy · pandas · PyArrow/Parquet · FastAPI with Server-Sent Events · Pydantic · Uvicorn
Dashboard & narration
HTML Canvas and vanilla JavaScript — no charting library, no tile service, nothing loaded from a CDN · optional Groq / Gemini / Ollama narration via httpx, with deterministic templates offline
Verification
pytest — 23 invariant tests asserting properties a real bug would break, including that the model never beats its own oracle
Approach, Algorithms & Tools
GridRecoveryIQ

## Slide 10
Completed for Review II
Network generator, hidden hazard model and three-year synthetic history
Risk model with oracle benchmark, time-ordered split and isotonic calibration
FLISR engine — isolation, islanding, CP-SAT tie transfer, partial pickup
Crew dispatch optimiser with nearest-first baseline for comparison
Live control-room dashboard, five-agent layer, 23 invariant tests passing
Planned before final review
Replace the kVA headroom proxy with an unbalanced load-flow check before committing a transfer
Re-plan against current switching state for simultaneous faults on one feeder
Learn repair-time distributions from work-order data rather than assuming them
Sensitivity study across storm severities and tie-switch densities
Project Plan & Milestone Progress
GridRecoveryIQ

## Slide 11
Pipeline Structure
GridRecoveryIQ
OFFLINE · build and train
Network generator
187 sections · 25 ties
Hidden hazard model
3 yr · 1.64 M rows
LightGBM + calibration
AUC 0.804 / ceiling 0.841
Ranked exposure
risk per section
LIVE · on a fault
FaultDiagnosis
cause · repair estimate
SelfHealAgent
FLISR + CP-SAT switching
DispatchAgent
CP-SAT crew routing
IncidentCommander
narrated decision trail
seconds
hours of work, ordered
Counterfactual engine · the same faults with no automatic switching and a nearest-first dispatcher
difference reported live as customer-minutes saved
Deterministic engines compute every number; agents only frame and narrate. The platform runs identically with no API key.